## bus
| name | vn_kv | type | zone | in_service
0 | AW | 10 | n |  | TRUE
1 | INFO | 10 | n |  | TRUE
2 | ETI | 10 | n |  | TRUE
3 | IST | 10 | n |  | TRUE
4 | IW | 10 | n |  | TRUE
5 | HdS | 10 | n |  | TRUE
6 | ARENA | 10 | n |  | TRUE
7 | HKW | 10 | n |  | TRUE
8 | WW | 10 | n |  | TRUE
9 | NWZ | 10 | n |  | TRUE
10 | MENSA | 10 | n |  | TRUE
11 | MPA | 10 | n |  | TRUE
12 | STP | 10 | n |  | TRUE
13 | DLR | 10 | n |  | TRUE
14 | ATRIUM | 10 | n |  | TRUE
15 | KLW | 10 | n |  | TRUE
16 | ZHI | 10 | n |  | TRUE
17 | HdM | 10 | n |  | TRUE
18 | RZ | 10 | n |  | TRUE
19 | Birkhof | 10 | n |  | TRUE
20 | IFB | 10 | n |  | TRUE
21 | VFG | 10 | n |  | TRUE
22 | VISUS | 10 | n |  | TRUE
23 | Bio | 10 | n |  | TRUE
24 | MIKRO | 10 | n |  | TRUE
25 | SPZ | 10 | n |  | TRUE
26 | HLRS 1 | 10 | n |  | TRUE
27 | HLRS 2 | 10 | n |  | TRUE
28 | KZS | 10 | n |  | TRUE
29 | IFKB | 10 | n |  | TRUE
30 | ZAQ | 10 | n |  | TRUE
31 | IFF | 10 | n |  | TRUE
32 | ILA2 RN | 10 | n |  | TRUE
33 | ES4 | 10 | n |  | TRUE
34 | AW Erw. | 10 | n |  | TRUE
35 | AW 2.Erw. | 10 | n |  | TRUE
36 | KZN | 10 | n |  | TRUE
37 | ENTE | 10 | n |  | TRUE
38 | ILA1 RN | 10 | n |  | TRUE
39 | IVK RN | 10 | n |  | TRUE
40 | OGI | 10 | n |  | TRUE
41 | Polizei | 10 | n |  | TRUE
42 | L3 RN | 10 | n |  | TRUE
43 | Statik | 10 | n |  | TRUE
44 | AERO | 10 | n |  | TRUE
45 | Muff_AW-INFO | 10 | m |  | TRUE
46 | Muff_INFO-ETI | 10 | m |  | TRUE
47 | Muff_AW-ZHI | 10 | m |  | TRUE
48 | Muff_HKW-DLR | 10 | m |  | TRUE
49 | Muff_DLR-ATRIUM | 10 | m |  | TRUE
50 | Muff_ZHI-HdM | 10 | m |  | TRUE
51 | Muff_AW-KZS1 | 10 | m |  | TRUE
52 | Muff_AW-KZS2 | 10 | m |  | TRUE
53 | Muff_IFF-ZAQ | 10 | m |  | TRUE
54 | Muff_ZAQ-IFKB | 10 | m |  | TRUE
55 | Batt1_Muff_AW-INFO | 0.4 | b | battery | TRUE
56 | Batt2_Muff_INFO-ETI | 0.4 | b | battery | TRUE
57 | Batt3_Muff_AW-ZHI | 0.4 | b | battery | TRUE
58 | Batt4_Muff_HKW-DLR | 0.4 | b | battery | TRUE
59 | Batt5_Muff_DLR-ATRIUM | 0.4 | b | battery | TRUE
60 | Batt6_Muff_ZHI-HdM | 0.4 | b | battery | TRUE
61 | Batt7_Muff_AW-KZS1 | 0.4 | b | battery | TRUE
62 | Batt8_Muff_AW-KZS2 | 0.4 | b | battery | TRUE
63 | Batt9_Muff_IFF-ZAQ | 0.4 | b | battery | TRUE
64 | Batt10_Muff_ZAQ-IFKB | 0.4 | b | battery | TRUE
65 | EnBW | 110 | n |  | TRUE
66 | ES1 | 10 | n |  | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | ETI-IST | N2XSY 1x240 RM 6/10 kV | 2 | 3 | 0.2 | 0.0754 | 0.10367 | 460 | 0 | 0.53 | 1 | 1 | cs | TRUE
1 | AW-NWZ 1 | A2YHSY 1x300 RM 6/10 kV | 0 | 9 | 0.31 | 0.1 | 0.10053 | 500 | 0 | 0.435 | 1 | 1 | cs | TRUE
2 | AW-NWZ 2 | A2YHSY 1x300 RM 6/10 kV | 0 | 9 | 0.31 | 0.1 | 0.10053 | 500 | 0 | 0.435 | 1 | 1 | cs | TRUE
3 | NWZ-MEN | NA2XS(F)2Y 1x300 RM/25 6/10 kV | 9 | 10 | 0.46 | 0.1 | 0.10336 | 495 | 0 | 0.467 | 1 | 1 | cs | TRUE
4 | NWZ-WW | NA2XS2Y 1x95 RM/16 6/10 kV | 9 | 8 | 0.23 | 0.32 | 0.12284 | 315 | 0 | 0.249 | 1 | 1 | cs | TRUE
5 | ETI-IW | A2YHSY 1x300 RM 6/10 kV | 2 | 4 | 0.35 | 0.1 | 0.10053 | 500 | 0 | 0.435 | 1 | 1 | cs | TRUE
6 | IW-HdS | N2XS(F)2Y 1x240 RM/25 6/10 kV | 4 | 5 | 0.3 | 0.0754 | 0.10619 | 456 | 0 | 0.524 | 1 | 1 | cs | TRUE
7 | HdS-ARENA | N2XS(F)2Y 1x240 RM/25 6/10 kV | 5 | 6 | 0.645 | 0.0754 | 0.10619 | 456 | 0 | 0.524 | 1 | 1 | cs | TRUE
8 | ARENA-HKW | N2XS(F)2Y 1x240 RM/25 6/10 kV | 6 | 7 | 0.41 | 0.0754 | 0.10619 | 456 | 0 | 0.524 | 1 | 1 | cs | TRUE
9 | MENSA-MPA | N2XS(F)2Y 1x300 RM/25 6/10 kV | 10 | 11 | 0.809 | 0.0601 | 0.10336 | 495 | 0 | 0.588 | 1 | 1 | cs | TRUE
10 | MPA-HKW | N2XS(F)2Y 1x300 RM/25 6/10 kV | 11 | 7 | 0.81 | 0.0601 | 0.10336 | 495 | 0 | 0.588 | 1 | 1 | cs | TRUE
11 | NWZ-STP | NA2XS(F)2Y 1x300 RM/25 6/10 kV | 9 | 12 | 0.51 | 0.1 | 0.10336 | 495 | 0 | 0.467 | 1 | 1 | cs | TRUE
12 | STP-DLR | N2XS(F)2Y 1x300 RM/25 6/10 kV | 12 | 13 | 0.929 | 0.0601 | 0.10336 | 495 | 0 | 0.588 | 1 | 1 | cs | TRUE
13 | DLR-Muff_HKW-DLR | N2XS(F)2Y 1x300 RM/25 6/10 kV | 13 | 48 | 0.469 | 0.0601 | 0.10336 | 495 | 0 | 0.588 | 1 | 1 | cs | TRUE
14 | DLR-Muff_DLR-ATRIUM | N2XS(F)2Y 1x95 RM/16 6/10 kV | 13 | 49 | 0.24 | 0.193 | 0.097012 | 310 | 0 | 0.32 | 1 | 1 | cs | TRUE
15 | HdM-RZ | A2YHSY 1x300 RM 6/10 kV | 17 | 18 | 0.61 | 0.1 | 0.10053 | 500 | 0 | 0.435 | 1 | 1 | cs | TRUE
16 | RZ-Birkhof | N2XSEY 3x95 RM/16 6/10 kV | 18 | 19 | 0.44 | 0.193 | 0.097012 | 310 | 0 | 0.307 | 1 | 1 | cs | TRUE
17 | RZ-KZS | A2YHSY 1x300 RM 6/10 kV | 18 | 28 | 0.26 | 0.1 | 0.10053 | 500 | 0 | 0.435 | 1 | 1 | cs | TRUE
18 | AW-IFB | A2YHSY 1x300 RM 6/10 kV | 0 | 20 | 0.31 | 0.1 | 0.10053 | 500 | 0 | 0.435 | 1 | 1 | cs | TRUE
19 | IFB-VFG | A2YHSY 1x300 RM 6/10 kV | 20 | 21 | 0.59 | 0.1 | 0.10053 | 500 | 0 | 0.435 | 1 | 1 | cs | TRUE
20 | VFG-Bio | NA2XS2Y 1x300 RM/25 6/10 kV | 21 | 23 | 0.74 | 0.1 | 0.10336 | 495 | 0 | 0.467 | 1 | 1 | cs | TRUE
21 | Bio-VISUS | NA2XS2Y 1x300 RM/25 6/10 kV | 23 | 22 | 0.42 | 0.1 | 0.10336 | 495 | 0 | 0.467 | 1 | 1 | cs | TRUE
22 | Bio-MIKRO | NA2XS2Y 1x300 RM/25 6/10 kV | 23 | 24 | 0.51 | 0.1 | 0.10336 | 495 | 0 | 0.467 | 1 | 1 | cs | TRUE
23 | MIKRO-SPZ | NA2XS2Y 1x300 RM 6/10 kV | 24 | 25 | 0.28 | 0.1 | 0.10336 | 495 | 0 | 0.467 | 1 | 1 | cs | TRUE
24 | MIKRO-KZS | NA2XS2Y 1x300 RM/25 6/10 kV | 24 | 28 | 0.16 | 0.1 | 0.10336 | 495 | 0 | 0.467 | 1 | 1 | cs | TRUE
25 | KZS-IFF | NA2XS2Y 1x300 RM/25 6/10 kV | 28 | 31 | 0.36 | 0.1 | 0.10336 | 495 | 0 | 0.467 | 1 | 1 | cs | TRUE
26 | IFKB-AW_Erw. | NA2XS2Y 1x300 RM/25 6/10 kV | 29 | 34 | 0.7 | 0.1 | 0.10336 | 495 | 0 | 0.467 | 1 | 1 | cs | TRUE
27 | HKW-L3 RN | NA2XS(F)2Y 1x300 RM/25 6/10 kV | 7 | 42 | 0.62 | 0.1 | 0.10336 | 495 | 0 | 0.467 | 1 | 1 | cs | TRUE
28 | HKW-AERO | NA2XS(F)2Y 1x300 RM/25 6/10 kV | 7 | 44 | 0.25 | 0.1 | 0.10336 | 495 | 0 | 0.467 | 1 | 1 | cs | TRUE
29 | AERO-Statik | NA2XS(F)2Y 1x300 RM/25 6/10 kV | 44 | 43 | 0.28 | 0.1 | 0.10336 | 495 | 0 | 0.467 | 1 | 1 | cs | TRUE
30 | Statik-L3 RN | NA2XS(F)2Y 1x300 RM/25 6/10 kV | 43 | 42 | 0.21 | 0.1 | 0.10336 | 495 | 0 | 0.467 | 1 | 1 | cs | TRUE
31 | HKW-KZN | A2YHSY 1x300 RM 6/10 kV | 7 | 36 | 0.08 | 0.1 | 0.10053 | 500 | 0 | 0.435 | 1 | 3 | cs | TRUE
32 | KZN-ENTE | NA2XSY 1x300 RM 6/10 kV | 36 | 37 | 0.31 | 0.1 | 0.10053 | 500 | 0 | 0.47 | 1 | 1 | cs | TRUE
33 | KZN-ILA1 RN | A2YHSY 1x300 RM 6/10 kV | 36 | 38 | 0.08 | 0.1 | 0.10053 | 500 | 0 | 0.435 | 1 | 1 | cs | TRUE
34 | ILA1 RN-ILA2 RN | A2YHSY 1x300 RM 6/10 kV | 38 | 32 | 0.02 | 0.1 | 0.10053 | 500 | 0 | 0.435 | 1 | 1 | cs | TRUE
35 | ILA1 RN-IVK RN | NA2XS(F)2Y 1x300 RM/25 6/10 kV | 38 | 39 | 0.26 | 0.1 | 0.10336 | 495 | 0 | 0.467 | 1 | 1 | cs | TRUE
36 | IVK RN-OGI | NA2XS(F)2Y 1x300 RM 6/10 kV | 39 | 40 | 0.575 | 0.1 | 0.10336 | 495 | 0 | 0.467 | 1 | 1 | cs | TRUE
37 | OGI-Polizei | N2XSY 1x95 RM/16 6/10 kV | 40 | 41 | 0.18 | 0.193 | 0.11938 | 320 | 0 | 0.32 | 1 | 1 | cs | TRUE
38 | OGI-HKW | A2YHSY 1x300 RM 6/10 kV | 40 | 7 | 0.42 | 0.1 | 0.10053 | 500 | 0 | 0.435 | 1 | 1 | cs | TRUE
39 | AW-Muff_AW-INFO | A2YHSY 1x300 RM 6/10 kV | 0 | 45 | 0.45 | 0.1 | 0.10053 | 500 | 0 | 0.435 | 1 | 1 | cs | TRUE
40 | Muff_AW-INFO-INFO | NYSEY 1x240 RM 6/10 kV | 45 | 1 | 0.08 | 0.0754 | 0.10524 | 1330 | 0 | 0.456 | 1 | 1 | cs | TRUE
41 | INFO-Muff_INFO-ETI | NYSEY 1x240 RM 6/10 kV | 1 | 46 | 0.08 | 0.0754 | 0.10524 | 1330 | 0 | 0.456 | 1 | 1 | cs | TRUE
42 | Muff_INFO-ETI-ETI | A2YHSY 1x300 RM 6/10 kV | 46 | 2 | 0.39 | 0.1 | 0.10053 | 500 | 0 | 0.435 | 1 | 1 | cs | TRUE
43 | Muff_HKW-DLR-HKW | N2XS(F)2Y 1x300 RM/25 6/10 kV | 48 | 7 | 0.715 | 0.0601 | 0.10336 | 495 | 0 | 0.588 | 1 | 1 | cs | TRUE
44 | Muff_DLR-ATRIUM-ATRIUM | N2XS(F)2Y 1x95 RM/16 6/10 kV | 49 | 14 | 0.148 | 0.193 | 0.097012 | 310 | 0 | 0.32 | 1 | 1 | cs | TRUE
45 | DLR-KLW | NKBA 3x95 | 13 | 15 | 1.45 | 0.193 | 0.084823 | 470 | 0 | 0.255 | 1 | 1 | cs | TRUE
46 | AW-Muff_AW-ZHI | A2YHSY 1x300 RM 6/10 kV | 0 | 47 | 0.246 | 0.1 | 0.10053 | 500 | 0 | 0.435 | 1 | 1 | cs | TRUE
47 | Muff_AW-ZHI-ZHI | NA2XS(F)2Y 1x300 RM/25 6/10 kV | 47 | 16 | 0.205 | 0.1 | 0.10336 | 495 | 0 | 0.467 | 1 | 1 | cs | TRUE
48 | ZHI-Muff_ZHI-HdM | NA2XS(F)2Y 1x300 RM/25 6/10 kV | 16 | 50 | 0.368 | 0.1 | 0.10336 | 495 | 0 | 0.467 | 1 | 1 | cs | TRUE
49 | Muff_ZHI-HdM-HdM | NA2XS(F)2Y 1x300 RM/25 6/10 kV | 50 | 17 | 0.115 | 0.1 | 0.10336 | 495 | 0 | 0.467 | 1 | 1 | cs | TRUE
50 | AW_Erw-Muff_AW-KZS1 | N2XSY 1x240 RM/25 6/10 kV | 34 | 51 | 0.01 | 0.0754 | 0.10367 | 460 | 0 | 0.53 | 1 | 1 | cs | TRUE
51 | Muff_AW-KZS1-Muff_AW-KZS2 | A2YHSY 1x300 RM 6/10 kV | 51 | 52 | 0.77 | 0.1 | 0.10053 | 500 | 0 | 0.435 | 1 | 1 | cs | TRUE
52 | Muff_AW-KZS2-KZS | NA2XS(F)2Y 1x300 RM/25 6/10 kV | 52 | 28 | 0.375 | 0.1 | 0.10336 | 495 | 0 | 0.467 | 1 | 1 | cs | TRUE
53 | IFF-Muff_IFF-ZAQ | NA2XS2Y 1x300 RM/25 30 kV | 31 | 53 | 0.62 | 0.1 | 0.10336 | 495 | 0 | 0.467 | 1 | 1 | cs | TRUE
54 | Muff_IFF-ZAQ-ZAQ | NA2XS2Y 1x300 RM/25 6/10 kV | 53 | 30 | 0.08 | 0.1 | 0.10336 | 495 | 0 | 0.467 | 1 | 1 | cs | TRUE
55 | ZAQ-Muff_ZAQ-IFKB | NA2XS2Y 1x300 RM/25 6/10 kV | 30 | 54 | 0.08 | 0.1 | 0.10336 | 495 | 0 | 0.467 | 1 | 1 | cs | TRUE
56 | Muff_ZAQ-IFKB-IFKB | NA2XS2Y 1x300 RM/25 30 kV | 54 | 29 | 0.1 | 0.1 | 0.10336 | 495 | 0 | 0.467 | 1 | 1 | cs | TRUE
57 | AW-HLRS1 | N2XSY 1x240 RM/25 6/10 kV | 0 | 26 | 0.96 | 0.0754 | 0.10367 | 460 | 0 | 0.53 | 1 | 1 | cs | TRUE
58 | HLRS1-HLRS2 | N2XSY 1x240 RM/25 6/10 kV | 26 | 27 | 0.192 | 0.0754 | 0.10367 | 460 | 0 | 0.53 | 1 | 1 | cs | TRUE
59 | HLRS2-AW_Erw. | N2XSY 1x240 RM/25 6/10 kV | 27 | 34 | 1.01 | 0.0754 | 0.10367 | 460 | 0 | 0.53 | 1 | 1 | cs | TRUE
60 | Aw_Erw-AW_Erw2 | N2XSY 1x300 RM/25 6/10 kV | 34 | 35 | 0.01 | 0.0601 | 0.10053 | 500 | 0 | 0.595 | 1 | 3 | cs | TRUE
61 | ES4-AW_Erw2 | N2XSY 1x500 RM/35 6/10 kV | 33 | 35 | 0.01 | 0.0366 | 0.089 | 610 | 0 | 0.739 | 1 | 4 | cs | TRUE
62 | AW-AW_Erw2 | N2XSY 1x300 RM/25 6/10 kV | 35 | 0 | 0.01 | 0.0601 | 0.10053 | 500 | 0 | 0.595 | 1 | 3 | cs | TRUE
63 | Batt1_Muff_AW-INFO | NAYY 4x150 SE | 45 | 55 | 0.01 | 0.0754 | 0.10367 | 460 | 0 | 0.53 | 1 | 1 | cs | TRUE
64 | Batt2_Muff_INFO-ETI | NAYY 4x150 SE | 46 | 56 | 0.01 | 0.0754 | 0.10367 | 460 | 0 | 0.53 | 1 | 1 | cs | TRUE
65 | Batt3_Muff_AW-ZHI | NAYY 4x150 SE | 47 | 57 | 0.01 | 0.0754 | 0.10367 | 460 | 0 | 0.53 | 1 | 1 | cs | TRUE
66 | Batt4_Muff_HKW-DLR | NAYY 4x150 SE | 48 | 58 | 0.01 | 0.0754 | 0.10367 | 460 | 0 | 0.53 | 1 | 1 | cs | TRUE
67 | Batt5_Muff_DLR-ATRIUM | NAYY 4x150 SE | 49 | 59 | 0.01 | 0.0754 | 0.10367 | 460 | 0 | 0.53 | 1 | 1 | cs | TRUE
68 | Batt6_Muff_ZHI-HdM | NAYY 4x150 SE | 50 | 60 | 0.01 | 0.0754 | 0.10367 | 460 | 0 | 0.53 | 1 | 1 | cs | TRUE
69 | Batt7_Muff_AW-KZS1 | NAYY 4x150 SE | 51 | 61 | 0.01 | 0.0754 | 0.10367 | 460 | 0 | 0.53 | 1 | 1 | cs | TRUE
70 | Batt8_Muff_AW-KZS2 | NAYY 4x150 SE | 52 | 62 | 0.01 | 0.0754 | 0.10367 | 460 | 0 | 0.53 | 1 | 3 | cs | TRUE
71 | Batt9_Muff_IFF-ZAQ | NAYY 4x150 SE | 53 | 63 | 0.01 | 0.0754 | 0.10367 | 460 | 0 | 0.53 | 1 | 4 | cs | TRUE
72 | Batt10_Muff_ZAQ-IFKB | NAYY 4x150 SE | 54 | 64 | 0.01 | 0.0754 | 0.10367 | 460 | 0 | 0.53 | 1 | 3 | cs | TRUE

## storage
name | bus | p_mw | max_e_mwh | soc_percent | min_e_mwh | in_service | scaling | control_strategy | max_p_mw | min_p_mw | efficiency_percent
Batt_Node_1 | 58 | 0 | 96.3 | 50 | 0 | TRUE | 1 | vanilla | 96.3 | -96.3 | 100
Batt_Node_2 | 59 | 0 | 96.3 | 50 | 0 | TRUE | 1 | vanilla | 96.3 | -96.3 | 100
Batt_Node_3 | 60 | 0 | 96.3 | 50 | 0 | TRUE | 1 | vanilla | 96.3 | -96.3 | 100
Batt_Node_4 | 61 | 0 | 96.3 | 50 | 0 | TRUE | 1 | vanilla | 96.3 | -96.3 | 100
Batt_Node_5 | 62 | 0 | 96.3 | 50 | 0 | TRUE | 1 | vanilla | 96.3 | -96.3 | 100
Batt_Node_6 | 63 | 0 | 96.3 | 50 | 0 | TRUE | 1 | vanilla | 96.3 | -96.3 | 100
Batt_Node_7 | 64 | 0 | 96.3 | 50 | 0 | TRUE | 1 | vanilla | 96.3 | -96.3 | 100
Batt_Node_8 | 65 | 0 | 96.3 | 50 | 0 | TRUE | 1 | vanilla | 96.3 | -96.3 | 100
Batt_Node_9 | 66 | 0 | 96.3 | 50 | 0 | TRUE | 1 | vanilla | 96.3 | -96.3 | 100
Batt_Node_10 | 67 | 0 | 96.3 | 50 | 0 | TRUE | 1 | vanilla | 96.3 | -96.3 | 100

## load
Unnamed: 0 | name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | Strahlenphysik | 12 | 0.08 | 0 | 0 | 0 |  | 1 | TRUE | wye
1 | Lehrstuhl für Bildschirmtechnik | 20 | 0.13 | 0 | 0 | 0 |  | 1 | TRUE | wye
2 | Verfügungsgebäude | 21 | 0.07 | 0 | 0 | 0 |  | 1 | TRUE | wye
3 | Institut für Keramische Bauteile | 29 | 0.08 | 0 | 0 | 0 |  | 1 | TRUE | wye
4 | Institut für Zeitmesstechnik & HSG-IMAT | 29 | 0.048 | 0 | 0 | 0 |  | 1 | TRUE | wye
5 | Hy-Solar | 22 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
6 | Sportinstitut | 25 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
7 | Sporthalle | 25 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
8 | Segal-Haus | 22 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
9 | Rechenzentrum 1 | 18 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
10 | Rechenzentrum 2 | 18 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
11 | Kältezentrale Süd | 28 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
12 | Rechenzentrum Baracke | 18 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
13 | Bioverfahrenstechnik | 23 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
14 | Pegasus | 23 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
15 | Industrielle Fertigung und Fabrikbetrieb | 31 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
16 | Höchstleistungsrechenzentrum | 26 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
17 | Demonstrationshaus | 40 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
18 | Chemiegebäude | 40 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
19 | Verwaltungsgebäude OGI | 40 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
20 | Lagerhalle 1 | 40 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
21 | Holzbau | 40 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
22 | Betonbau | 40 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
23 | Stahlbau | 40 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
24 | Großversuchshalle | 40 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
25 | Erdbau | 40 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
26 | Brandhalle | 40 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
27 | Lagerhalle 2 | 40 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
28 | Lüftungszentrale bei PFWR 4G | 40 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
29 | Simtech | 5 | 0.012 | 0 | 0 | 0 |  | 1 | TRUE | wye
30 | Simtech2 | 5 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
31 | Maschinenlabor | 38 | 0.2 | 0 | 0 | 0 |  | 1 | TRUE | wye
32 | Ingenieurwissenschaften BT/B100 | 4 | 0.061 | 0 | 0 | 0 |  | 1 | TRUE | wye
33 | Verwaltungsgebäude HKW | 7 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
34 | Kältezentrale Nord | 36 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
35 | Ingenieurwissenschaften BT/A100 | 4 | 0.24 | 0 | 0 | 0 |  | 1 | TRUE | wye
36 | Energietechnik | 37 | 0.08 | 0 | 0 | 0 |  | 1 | TRUE | wye
37 | Greenteam | 37 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
38 | Sporthalle Keltenschanze | 14 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
39 | Verbrennungsmotoren und KFZ-Wesen | 39 | 0.31 | 0 | 0 | 0 |  | 1 | TRUE | wye
40 | Windkanal | 39 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
41 | Leichte Fläche | 37 | 0.001 | 0 | 0 | 0 |  | 1 | TRUE | wye
42 | Arena 2036 | 6 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
43 | L1 Aero-Gas Institutsgebäude | 44 | 0.023 | 0 | 0 | 0 |  | 1 | TRUE | wye
44 | L1 Aero-Gas Hallenbau | 44 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
45 | L1 Aero-Gas Windkanal | 44 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
46 | Verfahrenstechnik und Dampfkesselwesen 1 | 44 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
47 | L2 Statik und Dynamik Institutsgebäude | 43 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
48 | L2 Statik und Dynamik Versuchshalle | 43 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
49 | Raumfahrtzentrum Baden-Württemberg | 42 | 0.08 | 0 | 0 | 0 |  | 1 | TRUE | wye
50 | Luftfahrt 3 Institutsgebäude | 42 | 0.12 | 0 | 0 | 0 |  | 1 | TRUE | wye
51 | Luftfahrt 3 Hallenbau | 42 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
52 | Hochhaus MPA | 11 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
53 | Halle MPA A | 11 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
54 | Halle MPA C | 11 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
55 | Halle MPA D | 11 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
56 | Prüfhalle MPA | 11 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
57 | Atrium | 14 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
58 | Strahlwerkzeuge | 3 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
59 | Mensa (nur Studentenräume) | 10 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
60 | Elektrotechnik 1 | 2 | 0.175 | 0 | 0 | 0 |  | 1 | TRUE | wye
61 | Elektrotechnik 2 | 2 | 0.125 | 0 | 0 | 0 |  | 1 | TRUE | wye
62 | großer Hörsaal PFWR 53 | 9 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
63 | NWZ I Chemie Hochhaus | 9 | 0.63 | 0 | 0 | 0 |  | 1 | TRUE | wye
64 | NWZ II Physik Hochhaus | 9 | 0.6 | 0 | 0 | 0 |  | 1 | TRUE | wye
65 | Telefonzentrale | 9 | 0.003 | 0 | 0 | 0 |  | 1 | TRUE | wye
66 | Internationales Zentrum | 12 | 0.007 | 0 | 0 | 0 |  | 1 | TRUE | wye
67 | Wasserbau / VEGAS | 8 | 0.027 | 0 | 0 | 0 |  | 1 | TRUE | wye
68 | 110 kV Station | 55 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
69 | Campus Guest 1 | 1 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
70 | Campus Guest 2 | 1 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
71 | Campus Guest 3 | 1 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
72 | Campus Guest 4 | 1 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
73 | Informatik | 1 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye

## motor
Unnamed: 0 | name | bus | pn_mech_mw | loading_percent | cos_phi | cos_phi_n | efficiency_percent | efficiency_n_percent | lrc_pu | vn_kv | scaling | in_service | rx
0 | Tandem_3.1_KZS | 28 | 540 | 100 | 0.89 |  | 96.8 |  |  | 10 | 1 | FALSE | 0.15
1 | Tandem_3.2_KZS | 28 | 540 | 100 | 0.89 |  | 96.8 |  |  | 10 | 1 | FALSE | 0.15
2 | Turbo_2_KZS | 28 | 895 | 100 | 0.88 |  | 95.1 |  |  | 10 | 1 | FALSE | 0.15
3 | T_31_KZN | 36 | 540 | 100 | 0.89 |  | 95.5 |  |  | 10 | 1 | FALSE | 0.25
4 | T_32_KZN | 36 | 540 | 100 | 0.89 |  | 95.5 |  |  | 10 | 1 | FALSE | 0.25

## gen
Unnamed: 0 | name | bus | p_mw | vm_pu | sn_mva | min_q_mvar | max_q_mvar | scaling | slack | in_service | slack_weight | type
0 | Generator G43 | 7 | 3 | 1 | 4 | -4 | 4 | 1 | FALSE | FALSE | 0 | sync
1 | Generator G5 | 7 | 12 | 1 | 16 | -16 | 16 | 1 | FALSE | FALSE | 0 | sync
2 | Generator G42 | 7 | 6 | 1 | 6 | -6 | 6 | 1 | FALSE | FALSE | 0 | sync
3 | Generator G6 | 7 | 12 | 1 | 15 | -15 | 15 | 1 | FALSE | FALSE | 0 | sync
4 | Generator G41 | 7 | 6 | 1 | 6 | -6 | 6 | 1 | FALSE | FALSE | 0 | sync

## switch
Unnamed: 0 | bus | element | et | type | closed | name | z_ohm | in_ka
0 | 33 | 33 | b | CB | TRUE | IS-Begrenzer | 0 | 2.5

## ext_grid
Unnamed: 0 | name | bus | vm_pu | va_degree | slack_weight | in_service
0 | EnBW | 55 | 1 | 0 | 1 | TRUE

## trafo
Unnamed: 0 | name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | T111 | 40 MVA 110/10 kV | 55 | 56 | 40 | 110 | 10 | 16.2 | 0.34 | 18 | 0.05 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## impedance
Unnamed: 0 | name | from_bus | to_bus | rft_pu | xft_pu | rtf_pu | xtf_pu | sn_mva | in_service
0 | T111_Drosselspule | 56 | 33 | 7.5e-05 | 0.006975 | 7.5e-05 | 0.006975 | 40 | TRUE

## bus_geodata
Unnamed: 0 | x | y | coords
0 | 9.1037 | 48.7437
1 | 9.1069 | 48.7452
2 | 9.1045 | 48.7467
3 | 9.1031 | 48.7471
4 | 9.1063 | 48.7466
5 | 9.1077 | 48.7466
6 | 9.1095 | 48.7487
7 | 9.1103 | 48.75
8 | 9.1043 | 48.7442
9 | 9.1051 | 48.7455
10 | 9.1029 | 48.7464
11 | 9.1022 | 48.7507
12 | 9.1012 | 48.7443
13 | 9.1008 | 48.7482
14 | 9.1043 | 48.7487
15 | 9.0898 | 48.7507
16 | 9.1021 | 48.7413
17 | 9.1005 | 48.7416
18 | 9.0946 | 48.7406
19 | 9.0969 | 48.7382
20 | 9.1012 | 48.7435
21 | 9.1001 | 48.7435
22 | 9.0968 | 48.7431
23 | 9.0973 | 48.7424
24 | 9.0939 | 48.7408
25 | 9.0948 | 48.7417
26 | 9.097 | 48.7397
27 | 9.0969 | 48.739
28 | 9.0934 | 48.7407
29 | 9.0992 | 48.7434
30 | 9.098 | 48.744
31 | 9.0958 | 48.7413
32 | 9.1114 | 48.7494
33 | 9.1038 | 48.7434
34 | 9.1026 | 48.7449
35 | 9.1026 | 48.7449
36 | 9.1119 | 48.75
37 | 9.113 | 48.7492
38 | 9.1114 | 48.7497
39 | 9.1147 | 48.7499
40 | 9.1108 | 48.7476
41 | 9.1088 | 48.7478
42 | 9.1039 | 48.7506
43 | 9.106 | 48.7505
44 | 9.108 | 48.7496
45 | 9.1072 | 48.7451
46 | 9.1072 | 48.7452
47 | 9.1018 | 48.7424
48 | 9.1032 | 48.7506
49 | 9.103 | 48.7485
50 | 9.1001 | 48.742
51 | 9.1026 | 48.7449
52 | 9.0966 | 48.7405
53 | 9.098 | 48.7436
54 | 9.0982 | 48.7436
55 | 9.1042 | 48.743
56 | 9.1039 | 48.7433

## line_std_types
Unnamed: 0 | c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV
A2YHSY 1x300 RM 6/10 kV | 500 | 0.1 | 0.10053 | 0.435 | cs | 300 | 0.00403 | MV
N2XS(F)2Y 1x240 RM/25 6/10 kV | 456 | 0.0754 | 0.10619 | 0.524 | cs | 240 | 0.00393 | MV
N2XS(F)2Y 1x300 RM/25 6/10 kV | 495 | 0.0601 | 0.10336 | 0.588 | cs | 300 | 0.00393 | MV
N2XS(F)2Y 1x95 RM/16 6/10 kV | 310 | 0.193 | 0.097012 | 0.32 | cs | 95 | 0.00393 | MV
N2XSEY 3x95 RM/16 6/10 kV | 310 | 0.193 | 0.097012 | 0.307 | cs | 95 | 0.00393 | MV
N2XSY 1x240 RM/25 6/10 kV | 460 | 0.0754 | 0.10367 | 0.53 | cs | 240 | 0.00393 | MV
N2XSY 1x240 RM 6/10 kV | 460 | 0.0754 | 0.10367 | 0.53 | cs | 240 | 0.00393 | MV
N2XSY 1x95 RM/16 6/10 kV | 320 | 0.193 | 0.11938 | 0.32 | cs | 95 | 0.00393 | MV
NA2XS(F)2Y 1x300 RM/25 6/10 kV | 495 | 0.1 | 0.10336 | 0.467 | cs | 300 | 0.00403 | MV
NA2XS(F)2Y 1x300 RM 6/10 kV | 495 | 0.1 | 0.10336 | 0.467 | cs | 300 | 0.00403 | MV
NA2XS2Y 1x300 RM 6/10 kV | 495 | 0.1 | 0.10336 | 0.467 | cs | 300 | 0.00403 | MV
NA2XS2Y 1x300 RM/25 30 kV | 495 | 0.1 | 0.10336 | 0.467 | cs | 300 | 0.00403 | MV
NA2XS2Y 1x300 RM/25 6/10 kV | 495 | 0.1 | 0.10336 | 0.467 | cs | 300 | 0.00403 | MV
NA2XS2Y 1x95 RM/16 6/10 kV | 315 | 0.32 | 0.12284 | 0.249 | cs | 95 | 0.00403 | MV
NA2XSY 1x300 RM 6/10 kV | 500 | 0.1 | 0.10053 | 0.47 | cs | 300 | 0.00403 | MV
NKBA 3x95 | 470 | 0.193 | 0.084823 | 0.255 | cs | 95 | 0.00393 | MV
NYSEY 1x240 RM 6/10 kV | 1330 | 0.0754 | 0.10524 | 0.456 | cs | 240 | 0.00393 | MV
N2XSY 1x300 RM/25 6/10 kV | 500 | 0.0601 | 0.10053 | 0.595 | cs | 300 | 0.00393 | MV
N2XSY 1x500 RM/35 6/10 kV | 610 | 0.0366 | 0.089 | 0.739 | cs | 500 | 0.00393 | MV

## trafo_std_types
Unnamed: 0 | i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
Unnamed: 0 | sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
Unnamed: 0 | fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
Unnamed: 0 | element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | motor | name | object
16 | motor | bus | int64
17 | motor | pn_mech_mw | float64
18 | motor | loading_percent | float64
19 | motor | cos_phi | float64
20 | motor | cos_phi_n | float64
21 | motor | efficiency_percent | float64
22 | motor | efficiency_n_percent | float64
23 | motor | lrc_pu | float64
24 | motor | vn_kv | float64
25 | motor | scaling | float64
26 | motor | in_service | bool
27 | motor | rx | float64
28 | gen | name | object
29 | gen | bus | uint32
30 | gen | p_mw | float64
31 | gen | vm_pu | float64
32 | gen | sn_mva | float64
33 | gen | min_q_mvar | float64
34 | gen | max_q_mvar | float64
35 | gen | scaling | float64
36 | gen | slack | bool
37 | gen | in_service | bool
38 | gen | slack_weight | float64
39 | gen | type | object
40 | switch | bus | int64
41 | switch | element | int64
42 | switch | et | object
43 | switch | type | object
44 | switch | closed | bool
45 | switch | name | object
46 | switch | z_ohm | float64
47 | switch | in_ka | float64
48 | ext_grid | name | object
49 | ext_grid | bus | uint32
50 | ext_grid | vm_pu | float64
51 | ext_grid | va_degree | float64
52 | ext_grid | slack_weight | float64
53 | ext_grid | in_service | bool
54 | line | name | object
55 | line | std_type | object
56 | line | from_bus | uint32
57 | line | to_bus | uint32
58 | line | length_km | float64
59 | line | r_ohm_per_km | float64
60 | line | x_ohm_per_km | float64
61 | line | c_nf_per_km | float64
62 | line | g_us_per_km | float64
63 | line | max_i_ka | float64
64 | line | df | float64
65 | line | parallel | uint32
66 | line | type | object
67 | line | in_service | bool
68 | trafo | name | object
69 | trafo | std_type | object
70 | trafo | hv_bus | uint32
71 | trafo | lv_bus | uint32
72 | trafo | sn_mva | float64
73 | trafo | vn_hv_kv | float64
74 | trafo | vn_lv_kv | float64
75 | trafo | vk_percent | float64
76 | trafo | vkr_percent | float64
77 | trafo | pfe_kw | float64
78 | trafo | i0_percent | float64
79 | trafo | shift_degree | float64
80 | trafo | tap_side | object
81 | trafo | tap_neutral | int32
82 | trafo | tap_min | int32
83 | trafo | tap_max | int32
84 | trafo | tap_step_percent | float64
85 | trafo | tap_step_degree | float64
86 | trafo | tap_pos | int32
87 | trafo | tap_phase_shifter | bool
88 | trafo | parallel | uint32
89 | trafo | df | float64
90 | trafo | in_service | bool
91 | impedance | name | object
92 | impedance | from_bus | uint32
93 | impedance | to_bus | uint32
94 | impedance | rft_pu | float64
95 | impedance | xft_pu | float64
96 | impedance | rtf_pu | float64
97 | impedance | xtf_pu | float64
98 | impedance | sn_mva | float64
99 | impedance | in_service | bool
100 | bus_geodata | x | float64
101 | bus_geodata | y | float64
102 | bus_geodata | coords | object

## parameters
Unnamed: 0 | version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1